# Appendix 2: General Legionella Controls (SOP’s) -Checklist

| Service | Task | Frequency | Inspected By | Date | Action taken (if applicable) |
| --- | --- | --- | --- | --- | --- |
| Hot water Services | Where hot water is generated in a boiler room check that it stored above 60O C | Daily |  |  |  |
|  | Check local electric water heaters supplying hot water are stored above 60OC and maintained for one hour. | Quarterly |  |  |  |
|  | Check temperatures in flow and return pipework at calorifiers. The return temperature must be greater than 50oC | Monthly |  |  |  |
|  | Appoint a competent contractor to visually check on internal surfaces of calorifiers for scale, if possible, and remove sludge and sediment. | Every 12 Months |  |  |  |
|  | Check water temperature of first and last taps on a circulating system on each loop. Hot water taps should reach 50oC within 1 minute after opening tap, (location of taps to be identified by competent person), where localised thermostatic mixing valves are fitted the temperature should be measured at the valve supply point with a contact thermometer. | Monthly |  |  |  |
| Cold Water Services | Check that the tank water temperature at the point furthest away from the ball (float) valve and that the water flowing from the valve is below 20oC. Check there is cross flow through the tank. Check the surface for evidence of biofilm | Every Six Months |  |  |  |
|  | Check that the water temperature of the first and last taps on a circulating system is below 20oC after running the water for up to two minutes (location of taps to be identified by a competent person) | Monthly |  |  |  |
|  | Visually inspect cold-water tanks and carryout remedial works where necessary, (lids sealed/lidded to prevent contamination) | Every 12 Months |  |  |  |
| Shower Outlets | Inspect and flush for 2 minutes. | Weekly |  |  |  |
| Shower Heads | Dismantle, clean/disinfect and descale showerheads and hoses. | Quarterly or more frequently as required. |  |  |  |
| Little used outlets, e.g. toilets and wash hand basins. | Flush through direct to drain before use and without producing aerosols or water spray. | Weekly |  |  |  |
| Spa pools/baths | Check filters – sand filters should be back washed daily | Daily |  |  |  |
|  | Check water treatment , pools should be continuously treated with an oxidising biocide | Three times daily |  |  |  |
|  | Drain down, clean and disinfect entire system | At least weekly |  |  |  |

# Appendix 2: Specific Risks (SOP’s) -Legionella Checklist

| Service | Task | Frequency | Inspected by & date | Action Taken (if applicable) |
| --- | --- | --- | --- | --- |
| Spray Humidifiers, air washers and wet scrubbers | Clean and disinfect spray humidifiers/air washers and make up tanks including all wetted surfaces, descaling as necessary | Six monthly |  |  |
|  | Confirm the operation of non-chemical water treatment (if present) | Weekly |  |  |
| Water Softeners | Clean and disinfect resin and brine tank – check with manufacturer what chemicals can be used to disinfect resin bed | Weekly |  |  |
| Sprinkler and hose reel systems | When witnessing tests of sprinkler blow-down and hose reels ensure that there is minimum risk of exposure to aerosols | As directed by risk assessment |  |  |
| Lathe and machine tool coolant systems | Clean and disinfect storage and distribution system | Six monthly |  |  |
| Horticultural misting systems | Clean and disinfect distribution pipework, spray heads and make up tanks including all wetted surfaces, descaling as necessary | Quarterly or more frequently as required. |  |  |
| Vehicle washes | Check filtration and treatment system, clean and disinfect system | See manufacturer’s instructions |  |  |
| Fountains and water features | Clean and disinfect ponds, spray heads and make up tanks including all wetted surfaces, descaling as necessary | Interval depending on condition and risk assessment |  |  |
| Cooling towers and evaporative condensers | Refer to See L8 ‘Control of Legionella Bacteria in Water Systems’ and associated technical guidance and HSG 274 |  |  |  |

NB	A water system includes all plant / equipment and components associated with that system. For example, all associated pipework, pumps, feed tanks, valves, showers, heat exchangers, quench tanks, chillers, etc.